|  | EUROPEAN COMMISSION Directorate General Joint Research Centre Institute for Energy and Transport – Unit F.04 |
| --- | --- |

30 July 2015

PUBSY JRC96912

JRC TECHNICAL REPORT

D2.21 R&D and Industrial Infrastructures

rev. 0

Deliverable D2.21 for the FP7 NC2I-R Project

Grant Agreement Number: 605167

M.A. Fütterer (JRC), C. Auriault (LGI), O. Baudrand (IRSN), G. Brinkmann (AREVA),
D. Hittner (AREVA), S. Knol (NRG), Th. Mull (AREVA), K. Stehlik (CVR),
D. Vanvor (BriVaTech), K. Verfondern (FZJ)

|  | For the Authors | Reviewed by | Verified by | Approved by Unit Head |
| --- | --- | --- | --- | --- |
| Name | M.A. Fütterer | K. Tuček | K.F. Nilsson | P. Hähner |
| Date |  |  |  |  |
| Signature |  |  |  |  |

NC2I-R

Combination of CP & CSA

Co-funded by the European Commission under the

Euratom Research and Training Programme on Nuclear Energy

within the Seventh Framework Programme

Theme: FISSION-2013-2.4.1

Support to the emergence of a possible European Research Initiative on co-generation

Grant Agreement Number: 605167

Start date: 01/10/2013 Duration: 24 Months

D2.21 R&D and Industrial Infrastructures

Authors: M.A. Fütterer (JRC), C. Auriault (LGI), O. Baudrand (IRSN),
G. Brinkmann (AREVA), D. Hittner (AREVA), S. Knol (NRG),
Th. Mull (AREVA), K. Stehlik (CVR), 
D. Vanvor (BriVaTech), K. Verfondern (FZJ)

NC2I-R – Issued on 30/07/2015 by JRC

NC2I-R – Contract Number: 605167

| Document title | D2.21 R&D and Industrial Infrastructures |
| --- | --- |
| Author(s) | M.A. Fütterer (JRC), Auriault (LGI), O. Baudrand (IRSN), G. Brinkmann (AREVA), D. Hittner (AREVA), S. Knol (NRG), Th. Mull (AREVA), K. Stehlik (CVR), D. Vanvor (BriVaTech), K. Verfondern (FZJ) |
| Number of pages | 24 |
| Document type | Deliverable |
| Work Package | WP2 |
| Document number | rev. 0 |
| Issued by | JRC |
| Date of completion | 30/07/2015 |
| Dissemination level | Confidential, only for consortium members (including the Commission Services) |

Summary

This deliverable compiles the input from the different contributors to WP2 related to R&D and Industrial Infrastructures required for the demonstration of Nuclear Cogeneration technology using High Temperature Gas-cooled Reactors.

The methodology used consisted in confronting a bottom-up with a top-down approach. In the bottom-up phase we have collected information on existing or former infrastructures. Examples for that are known subjects from different sources such as reports from commercial companies, research centers, or the OECD TAREF database. In a parallel top-down approach, the authors have produced a priority table of critical infrastructure items and have filled in the missing information using a variety of sources including scientific literature, conference proceedings (in particular the HTR conference series), networking, information from the Generation IV International Forum, web-browsing, expert opinion, personal communication and databases.

The information in this report enables the preparation of a gap analysis to identify those R&D and Industrial Infrastructures which are not available and which would need to be built. It also provides a clearer picture as to what NC2I can bring into international cooperation such as the GEMINI Initiative.

Approval

| Rev. | Date | First author | WP leader | Project Coordinator |
| --- | --- | --- | --- | --- |
| 0 | 30 July 2015 | M. Fütterer (JRC) | M. Fütterer (JRC) | T. Jackowski (NCBJ) |
|  |  | 30/07/2015 | 30/07/2015 |  |

Distribution list

| Name | Organisation | Comments |
| --- | --- | --- |
| P. Manolatos | EC DG RTD |  |
| All beneficiaries | NC2I-R | Through internet workspace |

Table of contents

1	Objective and Methodology	6

2	Main messages from received input documents	6

2.1	Tribology and Corrosion [1]	6

2.2	Experience from PNP-Project [2]	7

2.3	Experience on EVA – ADAM Nuclear Heat Transfer System [3]	10

2.4	Cost Assessment HTR Module 250 [4]	10

2.5	Past experience on IHX and SSV [5]	11

2.6	Past experience on Helium turbomachines [6]	11

2.7	Past experience on KVK Component Test Loop [7]	12

2.8	Past experience on Tritium [8]	14

2.9	Experimental facilities in support to HTR safety demonstration [10]	14

2.10	Experimental facilities and measurement techniques for gas cooling research and technology at KIT/INR [11]	16

2.11	U. Cleve, private communication July 2015 [12]	16

2.12	Th. Mull, private communication July 2015 [13]	16

3	Most critical R&D and industrial infrastructures	16

4	Conclusions	24

5	References	24

# Objective and Methodology

The objective of Task 2.2 was to map the current European capacities in support of the RD&D programme of NC2I. This includes the listing and mapping of R&D infrastructures that may be used for HTR and nuclear cogeneration R&D, the listing of industrial production infrastructures that may contribute to the NC2I demonstrator construction.

The methodology used consisted in confronting a bottom-up with a top-down approach. In the bottom-up phase we have collected information on existing or former infrastructures. Examples for that are known subjects from different sources such as reports from commercial companies, research centers, or databases.

In a parallel top-down approach, the authors have produced a priority table of critical infrastructure items and have filled in the missing information.

The following information sources were tapped:

- deliverables from technology projects such as ARCHER

- HTR-TN archive

- AK VHTR in Germany

- EU infrastructure projects (e.g. SUSEN, ALLEGRO)

- GIF documents

- OECD Task Group on Advanced Reactor Experimental Facilities (TAREF): https://www.oecd-nea.org/nsd/csni/taref.html

- OECD Research and test facilities database (RTFDB): https://www.oecd-nea.org/rtfdb/

- ADRIANA: http://adriana.ujv.cz/ 
ftp://ftp.cordis.europa.eu/pub/fp7/euratom-fission/docs/adriana-final-report_en.pdf

- MICANET ftp://ftp.cordis.europa.eu/pub/fp7/euratom-fission/docs/adriana-final-report_en.pdf

- EHRO-N (for human resources): http://ehron.jrc.ec.europa.eu/public-ehro-n-files

- networking

- expert consultation

The information in this report enables the preparation of a gap analysis to identify those R&D and Industrial Infrastructures which are not available and which would need to be built. It also provides a clearer picture as to what contributions NC2I can bring into international cooperation such as the GEMINI Initiative.

# Main messages from received input documents

## Tribology and Corrosion [1]

This report provides the results of German past experience with coatings inside test facilities and test components for the facilities ADI (HRB) and KVK (INTERATOM).This work represents AREVA GmbH contribution to NC2I-R Deliverable D2-12/D2-21.

Several parts of an HTR are subjected to relative motion under load, and wear protecting materials are needed. Within the scope of investigation programs in Germany the available wear resistant materials and coatings were compiled and, after a selection phase, subjected to wear tests under different loads in artificial HTR-environment. Also aging tests were performed in order to gain information about the interaction of the partners in a temperature range where diffusion controlled processes will occur. Thermal cycling tests provided information about bonding strength and sensitivity to cracking and spalling.

The suitable materials were classified into application temperature ranges where up to 600°C "standard" metal-based hard-facings as 75Ni-17Cr-3.1B-4.5Si-3.5Fe-1.0C and 50Ni-15Cr-32Mo-3.0Si could be applied, for 600 - 700°C chromium carbides in a metal matrix (Cr2C3/NiCr) are suitable, up to 850°C chromium carbides as duplex layer (Cr23C6 - Cr23C6 /NiCr) and up to 950°C stabilized ZrO2 on a NiCrAIY intermediate layer are applicable.

## Experience from PNP-Project [2]

Germany looks back on several decades of comprehensive Research & Development activities on non-electricity applications of nuclear power. Joint efforts between interested industries and research organizations starting in the 1970s and ending in the 1990s were basically centered around the High-Temperature Gas-Cooled Reactor (HTGR) which is deemed to represent a suitable concept for safe, efficient, and economic generation of both electricity and heat for high temperature industrial processes including the production of hydrogen and/or liquid hydrocarbons for the transportation sector.

With the FZJ located in the coal-rich State of Northrhine-Westfalia, a central task was here the utilization of nuclear energy in the heat-intensive processes of coal gasification. The “Prototype Plant Nuclear Process Heat” (PNP) project was launched in 1972 in cooperation with partners from the coal and the nuclear industries with the main objectives to upgrade the pebble-bed HTGR for high coolant outlet temperatures of 950°C and to develop and test respective heat exchanging components. As a result, process heat reactor concepts were completed for 3000 MWt plants and a 500 MWt prototype plant “PNP-500”.

Different methods of gasification for the two types of coal, hard coal and brown coal (lignite), have been developed to be connected to a process heat HTGR. In the steam–coal gasification process, the introduction of nuclear heat requires a heat transfer via two heat exchangers, the He-He IHX and the steam gasifier, in order to avoid the handling of coal and ash in the reactor containment. In the hydro-gasification process, coal is converted with hydrogen in an exothermal reaction into synthetic natural gas. The required hydrogen can be generated from methane by steam reforming. Both gasification processes were successfully demonstrated on pilot plant scale under simulated nuclear conditions, i.e., the process heat needed being transferred from 950°C-helium. In the NFE (nuclear long-distance energy) project, the production of nuclear hydrogen by steam reforming of methane for energy storage, transportation, and recovery of the stored energy was investigated. The process was experimentally verified under nuclear conditions in the test facilities EVA (single reformer tube) and EVA-II (tube bundles). Reaction tubes with dimensions typical for industrial plants were connected in a closed helium loop to an electrical heater with a power input of 10 MWe simulating the nuclear source. The experiments confirmed the expected thermodynamic and chemical processing behavior. All essential components were designed and constructed for a power level representative for large and medium-sized plants (~125 MW), including two types of IHX, hot gas duct, HT valve, water cooler, steam generator. They were successfully tested in the 10 MW range in the KVK component test loop demonstrating their industrial feasibility at a high reliability and an almost 100% availability. Both PNP and NFE projects were accompanied by an extensive research program on high temperature resistant materials. In addition, safety evaluation of the combined system was conducted targeting in particular the tritium contamination of the product and the consequences of potential explosions of flammable gas mixtures.

Economic studies at the end of the 1980s, however, showed that competitiveness of nuclear SNG from expensive German coal with the cheap oil and gas available at that time on the world markets was not given.

The results of the long-term PNP project in Germany confirmed the technical feasibility of allothermal, continuous coal gasification and the licensing capability of the nuclear process heat HTGR. The nuclear supported process promises a saving of 35-40% of the coal resources. The idea of construction of a PNP plant was eventually abandoned at the beginning of the 1990s due to the fact that the nuclear process would not be economically competitive with the conventional process under the given economic and environmental conditions at that time.

Some conclusions and recommendations from the PNP project in more detail are as follows:

- By the manufacture and successful operation of high temperature heat exchanging and heat-transporting components under simulated nuclear conditions, highly valuable practical experience with high-temperature helium plants on a representative scale has been acquired.

- The broad experimental program conducted in KVK and other related test facilities has demonstrated that both IHX components manufactured could be successfully operated on the 10 MW power level in steady state and under transient conditions and at maximum helium heating temperatures of 950°C (primary) and 900°C (secondary), respectively. The operation time of the helical tube bundle was more than 5000 h, that of the U-tube bundle was more than 4000 h. On the basis of the available experience, both IHX were considered appropriate to be designed for a power of 170 MW and an operation time of 140,000 h at 950°C. However, it still needs additional work for nuclear applications and qualification of these methods and materials.

- The comprehensive experimental program within the NFE project (EVA-I and EVA-II facilities, additional testing of kinetics, heat transfer, materials) has shown that the two helium heated steam reformer bundles with about 6 MW power, consisting of 30 (18) tubes have been tested successfully. The dimensions and design data of the reformer tubes and the catalyst were the same as for the nuclear application. The maximum temperature of the helium to heat the reformer tubes was 950°C at 4 MPa allowing reaction rates of 103 Nm3 CH4/(m3 catalyst h) (related to the catalyst volume in the reformer tubes) at 800°C, 4 MPa and H2O/CH4 = 4 on the reformer side. The operation time was more than 6000 h.

- The efficiency of the catalyst practically remained unchanged after some 1000 h of operation. There was no carbon deposition on the catalyst because of the chosen H2O/CH4 ratio of 4 in the process. The handling of different catalysts was tested with procedures which can be applied to a larger component.

- The helium-heated steam reforming process is well understood and tested on a large scale. This should allow the extrapolation by a factor of around 10 from the EVA-II plant to a helium heated reformer connected to a modular HTGR of 170 to 200 MWt. For larger powers, more reformer loops should be coupled to the reactor.

Furthermore the closed-cycle EVA/ADAM chemical energy transportation system based on the energy carrier hydrogen was demonstrated. The conversion of methane at the reaction conditions mentioned above is of the order of 65%. It corresponds nearly to the thermodynamic equilibrium.

- For steam reformer applications, hydrogen permeation was found to represent a problem that could be solved. For processes using an IHX the permeated quantities of hydrogen can be reduced even more. As long as the heat exchangers remain intact, even under conservative assumptions, the expected radioactivity on the secondary side remains small compared with the tritium concentration by permeation. With regard to the 5 Bq/g limit, it would not be exceeded in any of the operational states in the PR-500.

- In the qualification program for high temperature metallic materials, steam reformer lifetimes and IHX materials have been approved to achieve the required lifetime of more than 100,000 h. The specific data of the test components were very similar to those which are planned for the nuclear application. Gas temperatures, pressures and material temperatures in the KVK facility were even identical to those of the nuclear design. Also the predicted thermodynamic data of the heat exchanger designs have been confirmed by the experiments showing that average heat fluxes of around 40 kW/m² can be realized at reasonable pressure drops. Still, the experience gained so far has disclosed that the technical solution of material problems require further efforts in longer-term projects. There were also other influences, which are more of political nature, that may have had a strong impact on conduction and success of the PNP project:

  - Partners of the PNP project did not include potential operators, and no nuclear operator demonstrated interest in the HTGR prototype plant.

  - Technology policy of the responsible Federal Ministry was characterized by a wide distribution of grants trying to support activities of many institutions and companies. This eventually led to a fragmentation into many, often parallel projects and sub-projects.

  - The termination of the parallel HHT project as a result of the unsuccessfully operated HHV test facility at KFA (today: FZJ) had a negative impact insofar as financial support of the PNP project by the Federal Government was reduced.

  - The lack of demonstration and experience, e.g., by sacrificing smaller-scale test plants (for economic reasons) was thought to be compensated by theoretical studies and lab-scale testing. Theory received high ranking and was obviously overestimated. Progress was expected by a "scientification" of the project. It was believed that the technology of coal gasification to produce SNG or liquid fuels could be used economically (in those days) under certain conditions depending mainly on the location, the cost of coal, and the product and its price compared to the competitors natural gas and crude oil. The use of nuclear primary energy promises savings of ~35% of the coal resources, increase the specific SNG output, and reduce specific emissions of carbon and other pollutants to the atmosphere, respectively. The plan of construction of a PNP demonstration plant was eventually abandoned at the beginning of the 1990s, when economic analyses had shown that competitiveness of nuclear SNG from expensive German coal with the cheap oil and gas available at that time on the world markets was not given. Future activities may take benefit from a re-evaluation of the above mentioned studies on HTGR process heat applications by comparing against current technologies and market conditions. The goal should be to select promising applications under the current industrial practice within existing and evolving markets. Superior safety features and high reliability are considered prerequisites for the introduction of nuclear process heat and nuclear CHP.

## Experience on EVA – ADAM Nuclear Heat Transfer System [3]

The test facilities EVA II / ADAM II served the examination and demonstration of the key processes of

a nuclear energy transportation system:

- the methane reformation with steam with heat transfer from helium under HTR typical conditions and

- the appropriate return reaction, the methane forming, at temperatures between 300°C and up to 650°C.

The formulae of these chemical reactions are:

CH4 + H2O + ΔH1  3 H2 + CO (1)		ΔH1 = 206 kJ/mol at 298 K

CH4 + 2 H2O + ΔH2  4 H2 + CO2 (2)		ΔH2 = 165 kJ/mol at 298 K

The chemical reactions from the left to the right of the formulae (1) and (2) are the endothermic methane reformation; the counter direction describes the exothermic methane formation. Both reactions assume chemical equilibrium whereas with the specified process conditions, equilibrium is only achievable using special catalysts.

The report also provides feedback from operation and safety performance of test facilities and the dimensioning of such a facility to a VHTR.

## Cost Assessment HTR Module 250 [4]

Based on the analyses of an HTR-MODULE 200 in the 1990s, the investment cost assessment of an HTR-MODULE 250 was performed which breaks down as follows:

| Total Investment Costs | [MEUR] |
| --- | --- |
| - Management | 33.8 |
| - Balance of Plant (BOP) | 208.8 |
| - Buildings | 115.1 |
| - Electrical systems | 62.9 |
| - I&C | 150.5 |
| - Site | 55.7 |
| - NSSS | 304.0 |
| Total | 930.8 |

The HTR-MODULE 250 is a two-modular plant for cogeneration of power and process steam for chemical complexes.

The following items are important for the cost assessment:

- First-of-its-Kind HTR-MODULE 250 plant was considered

- Legal and economic conditions of Germany

- Plant is integrated in the site of the chemical complex

- Due to the special requirements the plant is equipped with two diverse process steam lines in parallel and two turbine sets

- Data: 500 MWth; 387.63 MWth(net) steam; 98.25MWel(net)

- Process steam: 19 bar, 250°C, 42.9 kg/s and 3.5 bar, 139°C,104.3 kg/s

- Operation: 7500 hours/year full load

- Operating time: 40 years

- The overall design is such that in case of a shutdown of one module always 50% of the steam and electricity are kept available

- In case there is no steam demand, the modules can and have to produce electricity in order to avoid a shutdown of the plant;

## Past experience on IHX and SSV [5]

This document defines the operating conditions with an Intermediate Heat Exchanger (IHX) used to transfer heat from the primary circuit to the secondary circuit of a High Temperature Reactor (HTR) with indirect cycle. The functions and requirements have been established for the pre-conceptual design of the PNP program.

In the design of a PNP-HTR, the IHX were located in component vessel at the side of the reactor vessel, the connection between the component vessel and the reactor vessel is provided by the coaxial cross duct. Depending on the IHX design mainly, the design of the component vessel could be different.

The Secondary Separation Valve – Hot (SSV-H) connected directly to the IHX-pressure-Vessel nozzles and the reference concept is provided. The connecting nozzles entering the IHX pressure vessel in the secondary part of the pressure vessel. This means the nozzles to the secondary loop are arranged only in the secondary envelope and not in the area with primary gas.

The design of the nozzles for the plant with tubular IHX is a little different. The secondary hot gas duct between the IHX-hot gas outlet and the SSV-H inlet is arranged in a coaxial design and this is important for the stress analysis because the secondary hot gas duct is classified as an internal and not as a pressure pipe.

The report also provides several design details and manufacturers for these components.

## Past experience on Helium turbomachines [6]

In Germany a comprehensive research and development program was initiated in 1968 for a Brayton (closed) cycle power conversion system. The program was for ultimate use with a high temperature, helium cooled nuclear reactor heat source (the HHT project) for electricity generation using helium as the working fluid. The program continued until 1982 in international cooperation with the United States and Switzerland. This document describes the designs and reports the results of testing activities that addressed the development of turbines, compressors, hot gas ducts, materials, heat exchangers and other equipment items for use with a helium working fluid at high temperatures.

The program involved two experimental facilities. The first was an experimental cogeneration power plant (district heating and electricity generation) constructed and operated by the municipal utility, Energieversorgung Oberhausen (EVO), at Oberhausen, Germany. It consisted of a fossil fired heater, helium turbines, compressors and related equipment. The second facility was the High Temperature Helium Test Plant (HHV) for developing helium turbo machinery and components at the Research Center Jülich (KFA). The heat source for the HHV derived from an electric motor-driven helium compressor.

In both facilities negative and positive experiences were gained. At initial commissioning operation difficulties were encountered with the EVO facility, including failure to meet fully the design power output of 50 MW. The reasons for these difficulties were identified and as far as economically feasible the difficulties were corrected. At the HHV some start-up problems also occurred, but were soon corrected. The research and development programs at both facilities can be judged successful and fully supportive of proofing the feasibility of the use of high temperature helium as a Brayton cycle working fluid for direct power conversion from a helium cooled nuclear reactor.

Unfortunately, the HHT project was terminated in Germany and both test facilities have been shut down. Except for life tests, the facilities accomplished their missions and delivered all expected information. If helium turbomachinery technology is reconsidered for power conversion from a helium cooled nuclear reactor, no unresolvable problems are anticipated as they would already have been identified in these turbomachine test facilities.

It is well known that the AVR reactor had an excellent performance record during its 20-year operation (approximately 127,000 hours) including 45,000 hours operation at 950 °C.

The KVK-plant was successfully operated for more than 20,000 h with peak temperatures up to 1050 °C and the EVA-II for more than 15,000 h at 950 °C. Both test facilities demonstrated that large sized, high temperature helium circuits can be operated safely and with a high availability (e. g. in the last three years of test operation the KVK showed an availability > 95 %).

## Past experience on KVK Component Test Loop [7]

This report describes the design and design changes and the experience gained from the high temperature Helium test facility KVK which was erected and operated at the INTERATOM site in Bergisch Gladbach near Cologne.

The purpose for the erection of the facility was to test components for the Project "Prototype Plant Nuclear Process Heat" (PNP) where lignite and hard coal should be gasified by means of high temperature provided by nuclear power.

The time needed for detailed design, erection and commissioning of the facility was 30 months. Operation started in August 1982. The test facility was operated for about ten years with high availability. Meanwhile it was decommissioned and is no longer available.

The Project "Prototype Plant Nuclear Process Heat" (PNP) had led to such extreme and new requirements to the heat generating and transfer system that many issues at that time were judged to be resolveable only by experiments.

This was the main reason for design and operation of the KVK, the operation of which should yield experience in the following fields:

- Strength properties of metallic components in the high temperature region if the scope of applicable codes and standards were exceeded

- Demonstration of component function ability

- Mechanical behaviour and thermal properties of thermal insulation

- Mixing of stratified gas jets of differing temperature in various geometric configurations

- Friction, wear and tear, and friction welding under simulated reactor conditions

- Behaviour and qualification of seals

- Optimization of cooling systems in the high temperature region

- Confirmation and verification of the theoretical design basis

- Vibration behaviour under all anticipated boundary conditions

- Integral behaviour of the test facility

- Detection of malfunction and incident propagation

The test facility was designed to meet the following fundamental requirements:

- The facility should allow total maturation of a component prior to its installation in the reactor

- The extrapolation factor between facility test object and reactor component should be minimized

- With respect to test objects the facility should allow maximum flexibility in decoupling of the

- mass flow, transient behaviour, leak tightness et al.

Components foreseen to be tested were:

- Steam generator

- Process steam superheater

- Decay heat removal systems

- Blowers

- Helical heat exchanger

- U-tube heat exchanger

- Primary and secondary gas pipe of the hot leg

- Primary hot leg bellow

- Secondary hot leg pipe bend

- Secondary hot leg valve

Design requirements were:

I. Thermal dynamic characteristics

- design temperature 950° C

- design pressure 40 bar

- design flow rate 3 kg/s

- min flow rate 0.6 kg/s

- max. gas temperature 1.000°C

- max. system pressure 46 bar

II. Transients

- Temperature transient ± 200 K/min

- Pressure transient normal 3 bar/s, max 5 bar/s

- Pressure difference primary/secondary 40 bar

- Pressure difference transient prim/secon 5 bar/s

- Overload test at 40 bar and 950°C with mass flow 3.2 kg/s

- Periodic transients 200 K ± 5 K/min from 950°C to 650°C to 950°C

- Slow-down of mass flow within 1 min to 0.21 kg/s

III. Operational flexibility

- Transient to decay heat removal

- Coast down of a blower causing gas back flow

- Simultaneous or staggered run down of both blowers causing gas back flow

- Following shut down of the heat exchanger: operation of the test facility with single-loop for component part tests

- Leak tightness measurement during operation using a carrier gas

- Flow rate primary/secondary independently variable

- Start-up and shut-down with transients up to 5 K/min through the whole temperature range

## Past experience on Tritium [8]

High temperature gas-cooled reactors (HTR), like all other reactors, will produce tritium.

Some of the tritium will be contained in plant process fluids and in plant gaseous and liquid releases. However, HTRs may also be used to provide process heat/steam for industrial use. Because of permeation through heat exchanger metals, fluids used to convey heat/steam from the HTR plant to the industrial facility using this heat/steam will contain small amounts of tritium.

The principal purposes of this report are to:

- describe the unique aspects of tritium behavior in HTRs;

- review precedents, including quantitative data, applicable to tritium management in HTRs.

The report also summarizes the tritium balance in the plant. More details were modeled and summarized e.g. in [9].

For licensing it has to be considered that a certain tritium load in the products steam or fuel gas is already given independent of the nuclear operation. Feedwater contamination (originating from former atomic weapons testing) contributes up to 26 mBq/g to the process steam and up to 56 mBq/g, respectively, to the product gases. Using fossil feedstock adds another 37 mBq/g of natural T contamination.

In Germany, it can be stated that for the investigated cogeneration applications with HTRs there were no problems found for licensing regarding the former German Radiological Protection Ordinance [StrlSchV 1987]. Even in latest version of the German Radiological Protection Ordinance [StrlSchV 2012] there is no ruling creating problems for HTR cogeneration plants.

In the USA, tritium that has penetrated the process fluid streams is considered a “byproduct material”, as defined in 10CFR30, and is regulated by the NRC.

Obviously, the elaboration of a more refined tritium control strategy for HTR requires the knowledge of the licensing conditions for new-build HTR, in particular the allowed chronic and accidental tritium release. As these limits affect system design, they should be known and approved well before the final design stage of a reactor. Any changes later on may necessitate design modifications with a very detrimental effect on timing and cost, as it was experienced during the construction of the THTR. Once those limits are known, the methodology presented in this report can be used to define the effort to be made by the different systems which influence the effectiveness of tritium control. Those are in particular helium and water purification, allowable water/steam leak rate, helium chemistry and permeation barriers on the steam generator tube walls.

## Experimental facilities in support to HTR safety demonstration [10]

This document presents a list of R&D infrastructures that may be used to support the development of a high temperature reactor with a cogeneration capability. It is an update of the results of the OECD TAREF project (2009), focusing on experimental facilities which could be used for R&D and qualification of the systems and components important for safety.

In 2009, the TAREF project gave an overview of the experimental facilities relevant to gas-cooled reactors and took into account the potential for coupling HTRs with high temperature processes and hydrogen production. In this frame, it has addressed the configurations featuring an intermediate heat exchanger (IHX) and a direct energy conversion cycle.

The results of TAREF can be completed by the list of the facilities operated for the purpose of the ARCHER project (2011-2015). Moreover, the power conversion layout envisaged in ARCHER (steam generator heated directly by the primary helium) leads to specific safety cases.

Lastly, work from the ADRIANA project has also been explored. ADRIANA was dedicated to fast reactors, but some infrastructures might be of interest for the HTR concept, as GFR and HTR have the helium coolant in common. Moreover, most of the facilities listed in ADRIANA work were not built for gas cooled fast reactor either (many are supporting the fusion program).

The produced list of infrastructures is not comprehensive, as it describes only major existing facilities. Moreover, it shall be completed by the facilities currently under development in eastern European countries (SUSEN project is an example).

In case of cogeneration, the main impact is coming from the additional operating transients induced by the variation in heat demand, meaning:

- variation of thermo-mechanical loading on the second barrier (tubes of the steam generators or heat exchangers),

- variation in primary helium temperature.

As far as licensing is concerned, the nuclear applicant will have to justify that sufficient design provisions are taken to protect the nuclear plant against external hazards potentially induced by industrial facilities (heat and electricity end-users) and back-up installations (boilers). In some cases, the models describing the effects of external hazards and the acceptance criteria will have to be validated (note that the related facilities are commonly used for non-nuclear applications).

Finally, the demonstration of acceptable tritium control in heat transfer fluids requires specific tests on fuel graphite matrix and material permeability (including the behavior of tritium in graphite).

To our knowledge, there is no experimental facility built specifically to test cogeneration capabilities. However, experiments in support of specific cogeneration issues would probably not require a dedicated test facility, as far as the existing ones would be able to fully cover the associated physical states of the plant. So the facilities listed address a broader scope than the needs linked strictly to cogeneration safety.

The list of facilities shows that many experimental installations are already available to support the development of an HTR prototype, building on synergies with gas fast reactor projects and fusion technology. In particular, most of the separate effects tests could already be performed in existing facilities. For fuel qualification, irradiation experiences and reheating tests have already been performed (in HFR Petten and in AGR at the Idaho National Laboratory).

However, for the qualification of the main reactor components important for safety or pertaining to the confinement barriers (isolation valves, heat exchangers, steam generators, control rod mechanisms, etc.), specific test rigs will be needed, like the helium loop built in South Africa for the PBMR program.

To go forward in the concept development, experimental facilities should be selected after the development of an HTR prototype design including the definition of its heat production performances. Given this data, the plant designer will have to test the technical solutions required by cogeneration, like the systems which would dampen the specific transients (load following, loss of heat delivery system, etc.) or the isolation devices. On a case by case basis, experiments might also be necessary to qualify the protections envisaged to cope with the external hazards induced by the vicinity of the end-user industry (effects of chemicals on electronic systems, sensitivity of detection systems, fire resistance, etc.). But methodology and criteria defined for the industry should then be applicable.

At this point, it must be recalled that the R&D results regarding the demonstration of fulfilment of the major safety objectives should be available before starting the licensing process. However, even considering the work that has been done in the past and the European projects, it seems obvious that further development of the HTR concept need to be backed by the operation of a prototype reactor.

## Experimental facilities and measurement techniques for gas cooling research and technology at KIT/INR [11]

This presentation summarizes the available technology and competences at the Institute for Neutron Physics and Reactor Technology (INR) at the Karlsruhe Institute of Technology in Germany. This comprises 5 helium loops and 4 air loops in the pressure range 0.3 – 11 MPa, in the temperature range 100 – 900°C, and in the flow-rate range 10 – 1400 g/s. While these installations are mainly used for the development of helium-cooled fusion blankets and high heat flux facilities, they could be used for testing certain components including instrumentation relevant for HTR applications.

## U. Cleve, private communication July 2015 [12]

Dr. Urban Cleve is a retired manager from a company which has designed and built the THTR-300 in Germany. He provided valuable hints on companies which were involved in the 1980s in the construction of THTR-300 components and the reactor itself. This information was added to the table presented in section 3 of this report.

## Th. Mull, private communication July 2015 [13]

Thomas Mull from AREVA GmbH has delivered information on heat exchangers and steam generators for the KVK project and the HTR Modul. This information was added to the table presented in section 3 of this report.

# Most critical R&D and industrial infrastructures

During an expert meeting of WP2 at CV Rez, the following table was set up as a top-down listing of critical infrastructures. Using the input provided by the contributors, the table below was completed.

Availability Check List for Critical Infrastructures and Competences
in view of HTGR Licensing, Demonstration and Deployment for Nuclear Cogeneration

| General Purpose | Specific Purpose | Owner/Location | Status | further information | Comment |
| --- | --- | --- | --- | --- | --- |
| Computer tools for licensing |  |  |  |  |  |
|  | - HTGR design tools | US: NEAMS project EU: HTR Code Package (HCP) prototype | under development under development | http://energy.gov/ne/downloads/nuclear-energy-advanced-modeling-and-simulation-neams-program-plan RWTH Hans-Josef Allelein, RWTH Aachen |  |
|  | - design standards | AREVA GmbH Westinghouse, Germany HTR GmbH | validated validated validated |  |  |
|  | - neutronics | numerous companies and universities | operational and validated | cf. ARCHER |  |
|  | - thermal-hydraulics (core bypass, hot streaking in lower plenum) | numerous companies and universities | operational and validated | cf. ARCHER |  |
|  | - thermo-mechanics | numerous companies and universities | operational and validated | cf. ARCHER |  |
|  | - seismic behavior (of graphite stack) | CEA (TAMARIS)? |  |  |  |
|  | - pebble flow | several companies and universities |  |  |  |
|  | - fuel performance code | AREVA/CEA FZJ INL | validated validated validated |  |  |
|  | - graphite performance | AMEC, new ASME code | validated |  |  |
|  | - lifetime assessment of components | manufacturers |  |  |  |
|  | HTGR design data - fuel (R/B vs. T and burn-up) |  |  |  |  |
|  | - materials (creep, fatigue etc.) |  |  |  |  |
|  | - graphite (properties, shrink/swell curve) | new ASME code | validated |  |  |
|  | - composites (irradiation and corrosion data, in particular for CFC) |  | missing but not urgent | cf. ExtreMat project |  |
| Fuel |  |  |  |  |  |
|  | Manufacturing | USA: BW China: INET? Russia: NUKEM Japan: NFI (Westinghouse) | active active mothballed mothballed |  |  |
|  | Quality Control | AREVA-F | qualified, mothballed |  |  |
|  | Irradiation with fission gas release measurement | HFR Petten ATR INL | active active |  |  |
|  | PIE | NRG Petten JRC-ITU Karlsruhe INL | active active active |  |  |
|  | KÜFA (safety) tests | JRC-ITU INL ORNL | active active active |  |  |
| Materials |  |  |  |  |  |
|  | Materials Data Bases | JRC-IET Petten ORNL USA | active active |  |  |
|  | High temperature steels/alloys | ASME code | active |  |  |
| Material test facilities |  |  |  |  |  |
|  | High temperature helium loops | INR/KIT Germany | active |  |  |
|  | Oxidation testing facilities |  |  |  |  |
|  | Manufacturing and Quality Control | SGL Germany Toyo Tanso Japan GrafTech France |  |  |  |
| Graphite |  |  |  |  |  |
|  | Irradiation | HFR Petten ATR INL |  |  |  |
|  | PIE incl. gamma scanning and radioactivity retention | NRG Petten JRC-ITU Karlsruhe INL ORNL |  |  |  |
| Components (design, manufacturing, qualification) |  | CVŘ, Řež,CZ INR/KIT, DE | active active | Helium loops |  |
|  | Pressure vessel | several including AREVA Creusot CFHI, SEC, China Erzhong + Dongfang Japan Steel Works | active active active active | an RPV for a large 600 MWth HTGR would require new, larger tooling | http://www.world-nuclear.org/info/Nuclear-Fuel-Cycle/Power-Reactors/Heavy-Manufacturing-of-Power-Plants/ |
|  | Circulator magnetic bearings (He atmosphere, high T, loads) | ABB/BBC, Alstom, Rolls Royce SKF-S2M General Atomics | active active - |  |  |
|  | Steam Generator | Sulzer Balcke-Dürr Steinmüller LURGI General Atomics/ Stearns-Roger |  |  |  |
|  | Intermediate Heat Exchanger | DIDIER Interatom/GHT Balcke-Dürr Steinmüller/Sulzer AlfaLaval Heatric |  |  |  |
|  | Hot gas duct | Becker Technologies |  |  |  |
|  | Isolation valves | BBC/Krupp Velan Inc.e Corp. RACO Klinger/KWU |  |  |  |
|  | Decay heat removal system | custom built |  |  |  |
|  | Filters and dust removal |  |  |  |  |
|  | Fuel handling system | General Atomics (block) |  |  |  |
|  | Control rods and drive | BBK General Atomics |  |  |  |
|  | Instrumentation for demonstration and commercial operation: - temperature - pressure - He flow-rate - He composition - neutron flux - stress/strain - burn-up | ABB General Atomics |  |  |  |
|  | - He purification system | CVŘ, Řež, CZ | active | Helium loop |  |
| Safety Demonstration Tests [10] |  |  |  |  |  |
|  | - thermal-hydraulics and passive afterheat removal | HE-FUS3 | ENEA http://web.brasimone.enea.it/tfd/hefus/hefus3.htm | Thermo-hydraulic testing Helium component testing LOCA, LOFA, power excursion, long term isothermal cooling flow, slow thermal cycling | Power: 1 MW He maximum temperature 530°C in test section |
|  |  | HELOKA-HP | KIT / http://www.inr.kit.edu/64.php Resp.: Dr. B.-E. Ghidersa (bradut-eugen.ghidersa@kit.edu) | Hydraulic testing of circuit components in helium: heat transfer tests | Pressure 10 Mpa, temperature up to 500°C and helium flow up to 1,4 kg/s |
|  |  | L-STAR | KIT http://www.inr.kit.edu/english/256.php Resp.:bradut-eugen.ghidersa@kit.edu | Hydraulic testing for heat exchange correlation Dust behaviour in gas flow | Two loops, equipped with high definition flow field measurement techniques. Tmax=700°C (small loop) |
|  |  | HEDYT | CEA Contact:nicolas.tauveron@cea.fr | Core thermal-hydraulics | Dynamic helium loop (850°C, 10 MPa) |
|  |  | HTHL | UJV http://www.emtr.eu/lvr.html | High temperature materials Fission product transport | In pile testing (LVR 15 reactor) |
|  |  | HEBLO | KIT Resp.: Dr. B.-E. Ghidersa (bradut-eugen.ghidersa@kit.edu) | Helium loop with test section | Dedicated to component testing (blanket) for fusion reactor (450°C, 8 MPa) |
|  |  | Scaled High Temperature Heat Transfer facility (S-HT²) | UC-Berkeley Per Peterson peterson@nuc.berkeley.edu | Heat transfer coefficients | Reduce temperature and simulant fluids |
|  |  | ITHEX | KIT Martin.lux@kit.edu | Heat transfer and turbulent flow studies to deliver a database for CFD code qualification | Studies of heat transfer in heat exchangers with mini channels geometries |
|  |  | High temperature test facility HTTF | Oregon State University http://ne.oregonstate.edu/high-temperature-test-facility-httf | Normal operation conditions Pressurized and depressurized conduction cool down simulation | ¼ scale model of a block type core |
|  |  | MASLWR | Oregon State University http://ne.oregonstate.edu/multi-application-small-light-water-reactor-maslwr | Idem Natural circulation startup, helical steam generator heat transfer performance, etc. |  |
|  |  | NSTF | ANL dlisowski@anl.gov | Validation of passive heat removal systems (ex.: vessel pit cooling circuits) Validation of radiative heat exchanges (specific heat flux meters) | Essential to the validation of the reactor cavity cooling system in passive mode. ½ scale in axial height of a typical gas cooled reactor Heating power: 220 kW |
|  |  | RCCS separate effects testing | University of Wisconsin manderson@engr.wisc.edu | Idem NTSF | Complementary to NTSF Coolant: water or air |
|  |  | DEDIFAR | CEA | Mock-up for leak before break assessment | Data for the feasibility of leak before break assessment in helium |
|  | - quality and integrity of barriers |  |  |  |  |
|  |  | HEMAT | KIT http://www.inr.kit.edu/english/92.php | Helium loop for materials tests Test of corrosion and erosion of materials at high temperature (up to 750°C) |  |
|  |  | TAMARIS | CEA http://www-tamaris.cea.fr/ alain.lemaoult@cea.fr | Core and reflector stability under seismic loadings | Vibrating platform |
|  | - reactivity and power control |  |  |  |  |
|  |  | Annular core research reactor (ACRR) | Sandia National Laboratory http://www.sandia.gov/research/facilities/annular_core_research_reactor.html | Simulation of power transients (normal and abnormal) and power profiles |  |
|  |  | MASURCA | CEA bernard.autran@cea.fr | Critical mock-up | Adaptable to gas reactors (ex.: former program ENIGMA dedicated to GFR) Under refurbishment : restart not before 2019 |
|  |  | NSRR | JAEA | Power excursion: test of the robustness of the particles in case of fast reactivity insertion | Modified TRIGA reactor Pulse irradiation test of fresh and irradiated HTR fuel performed (1994 and 2006-2008) Fuel testing under fast reactivity transient would be needed since demonstration exhibited within the German licensing process of the HTR Module was based on ancient US experiments with differing fuel coatings. |
|  | - fission product inventory and transport |  |  |  |  |
|  |  | HFR | owned by JRC-IET Petten, NL operated by NRG Petten, NL | Qualification of HTR fuel (compacts and pebbles) by high burn-up high temperature neutron irradiation with online fission gas release analysis | 40 years of experience with HTGR fuel irradiation tests at JRC for the German fuel qualification program |
|  |  | KÜFA | JRC-ITU Karlsruhe, D | Post irradiation heating with on line analysis of fission products release; original installation from FZJ | Temperature up to 1800°C Equivalent installation at CEA: MERARG in LECA-STAR laboratory |
|  |  | ATR | INL mailto:jeff.benson@inl.gov | Qualification of HTR fuel compacts by high burn-up high temperature neutron irradiation with online fission gas release analysis | AGR irradiation program ongoing |
|  | - primary circuit depressurization and water/air ingress accidents |  |  |  |  |
|  |  | DUSTEX | KIT / https://www.iket.kit.edu/english/375.php | Gas/Dust mixtures explosion indices | Used for fusion program Risk due to flammable gases produced by graphite oxidation |
|  |  | Spherical bomb | CNRS/ICARE (Orleans) Nabiha Chaumeix chaumeix@cnrs-orleans.fr | Gas mixture flammability limits | Idem supra Similar facility available at KIT |
|  |  | A2 | KIT mike.kuznetsov@kit.edu | Gas and dust behaviour in containment | Part of LACOMEO facility dedicated to core degradation an containment behaviour (PWR) |
|  |  | MISTRA | CEA Saclay | Effects of gas mixing, test of mitigation technics | Simulation of a PWR containment in case of severe accident Study of thermohydraulics in confinement and risk of hydrogen explosion |
|  |  | NACOK II | damaged beyond repair FZJ / http://www.fz-juelich.de/iek/iek-6/DE/ueberuns/ansprechpartner/_node.html | Large scale test of graphite corrosion in air or other gas mixtures (excluding steam), heat transfer in pebble beds or block arrangements. Simulation of forced flow or natural circulation limited by a downcomer representing side reflector coolant holes. | Recently upgraded, used within the ARCHER project for separate effects test of Boudouard reaction. Now damaged |
|  |  | GOLab | FZJ | Graphite oxidisation laboratory | Small scale studies on graphite and carbon based materials oxidation phenomena |
|  |  | Induction experiment facility (INDEX) | FZJ | Provision of data for CFD validation for helium flow modelling in pebble bed or other geometries. | Small facility equipped with PIV and electrical heating system Used for ARCHER project |
|  |  | ESTHAIR | CEA / http://www-cathare.cea.fr/scripts/home/publigen/content/templates/show.asp?P=162&L=FR&SYNC=Y | “test section” for hydraulic testing in air (similitude conditions), low pressure | Study of potential natural circulation in case of break in primary circuit. Need to be adapted to HTR |
|  |  | HETIMO (He thermal insulation mock-up) | CEA / http://www-cadarache.cea.fr/fr/activites/fission/dtn/Plateformes/Gaz/Bancs/Hethimo.php | Qualification of thermal shielding conductance Simulation of fast depressurisation transients | Built for GFR concept developement Depressurisation transients up to 2 MPa/s |
|  |  | THAI | Becker Technologies info@becker-technologies.com | Transport and spatial distribution behaviour of graphite aerosol in single and multi compartment arrangements | Temperature up to 180°C and pressure up to 1,4 MPa |
|  | - dust production and behavior |  |  |  |  |
|  |  | Dresden Tube | TU Dresden wolfgang.lippmann@tu-dresden.de | dust mobilization and redeposition test |  |
|  |  | Dresden Tank | TU Dresden wolfgang.lippmann@tu-dresden.de |  |  |
|  | - tritium control | Tritium Laboratory Karlsruhe | KIT | https://www.itep.kit.edu/english/258.php | several relevant installations listed here; main orientation is fusion technology |
| Competences | designers (neutronics, thermo-mechanic, thermal-hydraulics, system analysis) economists licensing experts business model developers | European Human Resource Observatory – Nuclear (EHRO-N) European Nuclear Education Network (ENEN) | http://ehron.jrc.ec.europa.eu/ http://www.enen-assoc.org/ |  |  |
| Waste | Waste management for fuel | JRC-IET SelFrag CVŘ, Řež,CZ SRNL | needs qualification needs qualification starting up starting up | http://susen2020.cz/en/research/program-no-3-nuclear-fuel-cycle/ |  |
|  | Waste management for graphite | JRC-IET FZJ | needs hot qualification activity closed |  |  |

# Conclusions

This deliverable compiles the input from the different contributors to WP2 related to R&D and Industrial Infrastructures required for the demonstration of Nuclear Cogeneration technology using High Temperature Gas-cooled Reactors.

The methodology used consisted in confronting a bottom-up with a top-down approach. In the bottom-up phase we have collected information on existing or former infrastructures. Examples for that are known subjects from different sources such as reports from commercial companies, research centers, or the OECD TAREF database. In a parallel top-down approach, the authors have produced a priority table of critical infrastructure items and have filled in the missing information using a variety of sources including scientific literature, conference proceedings (in particular the HTR conference series), networking, information from the Generation IV International Forum, web-browsing, expert opinion, personal communication and databases.

The information in this report enables the preparation of a gap analysis to identify those R&D and Industrial Infrastructures which are not available and which would need to be built. It also provides a clearer picture as to what NC2I can bring into international cooperation such as the GEMINI Initiative.

Possible criteria for prioritization suggested for the gap analysis from Task 2.3 are:

- relevance for licensing

- bottlenecks, e.g. waiting queues for RPV production

- cost

- risk

- benefit

# References

- G. Brinkmann, D. Vanvor, K. Verfondern, Earlier Experience from Germany - Tribology and Corrosion, AREVA and FZJ contribution to deliverable D2-12/D2-21, 19 June 2014.

- G. Brinkmann, D. Vanvor, K. Verfondern, Experience from PNP-Project at FZJ, AREVA and FZJ contribution to deliverable D2-12/D2-21, 4 July 2014.

- G. Brinkmann, D. Vanvor, K. Verfondern, Earlier Experience from Germany - EVA – ADAM Nuclear Heat Transfer System, AREVA and FZJ contribution to deliverable D2-12/D2-21, October 2014.

- G. Brinkmann, Th. Mull, D. Vanvor, Cost Assessment HTR Module 250, AREVA contribution to deliverable D2-12/D2-21, October 2014.

- G. Brinkmann, D. Vanvor, K. Verfondern, Past experience on IHX and SSV, AREVA and FZJ contribution to deliverable D2-12/D2-21, November 2014.

- G. Brinkmann, D. Vanvor, K. Verfondern, Past experience on Helium turbomachines, AREVA and FZJ contribution to deliverable D2-12/D2-21, October 2014.

- G. Brinkmann, D. Vanvor, K. Verfondern, Past experience on KVK Component Test Loop, AREVA and FZJ contribution to deliverable D2-12/D2-21, 1 September 2014.

- G. Brinkmann, D. Vanvor, K. Verfondern, Past experience on Tritium, AREVA and FZJ contribution to deliverable D2-12/D2-21, October 2014.

- E. D'Agata, M. A. Fütterer, Tritium Transport Modeling for High Temperature Reactors, 	Deliverable D23.71 for ARCHER SP2, JRC 83536, September 2013.

- O. Baudrand, Experimental facilities in support to HTR safety demonstration, IRSN report SRDS/SNR/2015/00022, July 2015.

- F. Arbeiter, B. Ghidersa, W. Hering, Experimental facilities and measurement techniques for gas cooling research and technology at INR, KIT presentation, July 2015.

- U. Cleve, private communication July 2015.

- Th. Mull, private communication July 2015.